Completed Fire Stopping Works Report

| Site Address: | {{address}} |
| --- | --- |
| Customer: | Northampton Partnership Homes |
| Date: | Thursday, 29 January 2026 |

Key

| Required Fire Rating | Definition |
| --- | --- |
| 30 Min F/S Infill | 30-minute fire compartment, Fire Stopping, Infill – ablative batt and intumescent mastic to be utilised to seal the void within the substrate, usually used for a solid substrate. |
| 30 Min Pattress Fix | 30-minute fire compartment, Fire Stopping, Pattress – ablative batt and intumescent mastic to be utilised to seal the void, mechanically fixed onto substrate with a minimum of 100mm overlap, usually used to protect a cavity walls. |
| 60 Min F/S Infill | 60-minute fire compartment, Fire Stopping, Infill – ablative batt and intumescent mastic to be utilised to seal the void within the substrate, usually used for a solid substrate. |
| 60 Min Pattress Fix | 60-minute fire compartment, Fire Stopping, Pattress – ablative batt and intumescent mastic to be utilised to seal the void, mechanically fixed onto substrate with a minimum of 100mm overlap, usually used to protect a cavity walls. |
| 120 Min F/S Infill | 120-minute fire compartment, Fire Stopping, Infill – ablative batt and intumescent mastic to be utilised to seal the void within the substrate, usually used for a solid substrate. |
| 120 Min Pattress Fix | 120-minute fire compartment, Fire Stopping, Pattress – ablative batt and intumescent mastic to be utilised to seal the void, mechanically fixed onto substrate with a minimum of 100mm overlap, usually used to protect a cavity walls. |
| Acoustic Seal | Seal to be completed for acoustic protection only. |

| Installation Type | Description / Installation & Materials required |
| --- | --- |
| PEGM | Pressure exerting graphite mastic, |
| Batt LN | Void which is over the length of a linear metre, One layer of ablative batt, sealed both sides with intumescent mastic, multi coat. |
| Batt LN (double layer). | As above, when access is only possible from one side. Two layers of ablative batt, sealed from one side with intumescent mastic, multi coat. Two layers are required to ensure that a double mastic seal is achieved. |
| Trapezoidal | Void at the head of a wall to the underside of soffit profile. One layer of ablative batt, intumescent mastic, multi coat |
| Trapezoidal (double) | As above, when access is only possible from one side. Two layers of ablative batt, intumescent mastic, multi coat. |
| Mastic LN metre | Void which is over the length of a linear metre up to 10mm wide. Seal void with intumescent mastic. |
| Cable | A single cable breaching through substrate. Intumescent mastic or PEGM can utilised to seal cables dependent on size and type. |
| Cable tray | Cable trays are sealed using ablative batt and mastic, where penetrations require a closure PEGM (pressure exerting graphite mastic) is utilised. |
| Cable bunch | Two or more cables grouped together breaching through a substrate. Intumescent mastic or PEGM can utilised to seal cables dependent on size and type. |
| Cable trunking | Capped cable trunking is sealed using ablative batt and mastic, an intumescent pad or intumescent pillow is installed within the trunking. |
| Duct | Where ducting passes through a fire line we would normally expect to see a fire/smoke damper installed. A smoke seal can be achieved utilising intumescent mastic. |
| Conduit | A plastic or metal tube of a diameter no more than 25mm. Intumescent mastic or PEGM/ pipe collar utilised to seal. |
| Metal pipe | Metal pipe of any diameter penetrating substrate, sealed with intumescent mastic, up to a maximum of 10mm between pipe and substrate. Any larger void will require ablative batt as part of the installation |
| Pipe hole | Redundant pipe hole, can be sealed with intumescent mastic and ablative batt dependent size. |
| Cable hole | Redundant cable hole, can be sealed with intumescent mastic and ablative batt dependent size. |
| Plastic pipe | Plastic pipe of any size and material base passing through a cavity void, wall, ceiling or floor, Sealed with intumescent mastic / endless wrap / graphite mastic / pipe sleeves / pipe collars dependent of substrate, type and size. |
| Insulated metal pipe | Insulation can either be removed and replaced with a fire sleeve or a closure can be attached utilising either endless wrap, PEGM or a pipe collar (solution dependent on pipe and insulation size). |
| Hole | Ablative batt installed to close the void, sealed with intumescent mastic, penetrations dealt with separately. |
| Quantity | Number of penetrations or metres, i.e. for Mastic LN Metre a quantity of 8 would require 8 linear metres of intumescent mastic. |
| Girths | The size of the void for infills or required batt for a pattress. |

| {{#seals}} SEAL ID {{seal_id}} |  |  |  |
| --- | --- | --- | --- |
| Fire Rating: | {{fire_rating}} | Location: | {{location}} |
| Operative: | {{operative}} | Access: | {{access}} |
| Fitting Detail: | {{fitting_detail}} | Substrate: | {{substrate.type}} |
| Substrate Type: | {{substrate.material}} |  |  |

| {{#seal_items}} Seal Type | {{seal_type}} |
| --- | --- |
| Installation Type | {{installation_type}} |
| X (mm) | {{x_mm}} |
| Y (mm) | {{y_mm}} |
| Quantity | {{quantity}} |
| Manufacturer | {{manufacturer}} {{/seal_items}} |

Works Details

| Works Date | {{works.date}} |
| --- | --- |
| Works Details | {{works.details}} |

PHOTOGRAPHIC EVIDENCE

BEFORE PHOTO

{{photos.before}}

AFTER PHOTO

{{photos.after}}

{{/seals}}